{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":37,"n_cols":8,"rows_kept":37,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","2MXM-N"]
[]
[]
[]
[]
["","","","","","2MXM40N2V1B","2MXM50N2V1B","2MXM68N2V1B"]
["Διαστάσεις","Μονάδα","","Διαστάσεις-=-Μονάδα-=-Ύψος-=-χιλ.","mm","550","550","734"]
["","","","Διαστάσεις-=-Μονάδα-=-Πλάτος-=-χιλ.","mm","765","765","958"]
["","","","Διαστάσεις-=-Μονάδα-=-Βάθος-=-χιλ.","mm","285","285","340"]
["Βάρος","Μονάδα","","","kg","36","41","60"]
["Κινητήρας ανεμιστήρα","Ταχύτητα","Ψύξη","Κινητήρας ανεμιστήρα-=-Ταχύτητα-=-Ψύξη-=-Εξαιρετικά χαμηλές-=-σ.α.λ.","σ.α.λ.","500","500","420"]
["","","Θέρμανση","Κινητήρας ανεμιστήρα-=-Ταχύτητα-=-Θέρμανση-=-Εξαιρετικά χαμηλές-=-σ.α.λ.","σ.α.λ.","320","500","420"]
["Συμπιεστής","Τύπος","","","","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing"]
["Εύρος λειτουργίας","Ψύξη","Περιβάλλοντος","Ελάχ.","°CDB","","","-10"]
["","","","Μέγ.","°CDB","","","46"]
["Στάθμη ηχητικής πίεσης","Ψύξη","","Υψ.","dBA","46","48"]
["","","","Ονομ.","dBA","","","48"]
["","Θέρμανση","","Υψ.","dBA","48","50"]
["","","","Ονομ.","dBA","","","48.0"]
["Ψυκτικό μέσο","Τύπος","","","","R-32","R-32","R-32"]
["","Φορτίο","","","kg","0.88","1.15","2"]
["","Φορτίο","","","tCO2Eq","0.60","0.78","1.35"]
["","GWP","","","","675","675","675.0"]
["Συνδέσεις σωληνώσεων","Μήκος σωληνώσεων","Μέγ.","OU - IU","m","20","20","25"]
["","Πρόσθετο φορτίο ψυκτικού","","","kg/m","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 30 m)"]
["","Υψομετρική διαφορά","ΕΣ.-ΕΞ.","Μέγ.","m","15.0","15.0","15.0"]
["","","ΕΣ.-ΕΣ.","Μέγ.","m","7.5","7.5","7.5"]
["","Συνολικό μήκος σωληνώσεων","Σύστημα","Πραγματικό","m","30","30","50"]
["Στάνταρτ εξαρτήματα","Installation manual","","","","1","1","1"]
["","Drain plug","","","","1","1","1"]
["","Screw bag","","","","1","1","1"]
["Τροφοδοσία ισχύος","Φάση","","","","1~","1~","1~"]
["","Συχνότητα","","","Hz","50","50","50"]
["","Τάση","","","V","220-230-240","220-230-240","220-240"]
["Σημειώσεις","","","","","(1) - Για ένα δωμάτιο","(1) - Για ένα δωμάτιο","(1) - Για ένα δωμάτιο"]
["Στάνταρτ εξαρτήματα","Reducer assembly","","","","","1","1"]
["","Drain cap","","","","","","3"]