{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":56,"n_cols":11,"rows_kept":56,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","2MXS-H"]
[]
[]
[]
[]
["","","","","","2MXS40H3V1B2","2MXS40H3V1B","2MXS40H2V1B","2MXS50H3V1B2","2MXS50H3V1B","2MXS50H2V1B"]
["Στάθμη ηχητικής πίεσης","Θέρμανση","","Ονομ.","dBA","48","48","","50","50"]
["","Ψύξη","","Ονομ.","dBA","47","47","","48","48"]
["Στάνταρτ εξαρτήματα","Εγχειρίδιο εγκατάστασης","","","","1","1","","1","1"]
["","Βιδωτή σακούλα","","","","1","1","","1","1"]
["","Τάπα εξόδου αποστράγγισης συμπυκνωμάτων","","","","1","1","","1","1"]
["Ψυκτικό μέσο","Charge","","","TCO2Eq","2.5","2.5","","3.3","3.3"]
["","GWP","","","","2,087.5","2,087.5","","2,087.5","2,087.5"]
["","Charge","","","kg","1.20","1.20","","1.60","1.60"]
["","Τύπος","","","","R-410A","R-410A","","R-410A","R-410A"]
["Piping connections","Υψομετρική διαφορά","ΕΣ.-ΕΣ.","Μέγ.","m","7.5","7.5","","7.5","7.5"]
["","","ΕΣ.-ΕΞ.","Μέγ.","m","15","15","","15","15"]
["","Πρόσθετο φορτίο ψυκτικού","","","kg/m","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)","","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)"]
["","Συνολικό μήκος σωληνώσεων","Σύστημα","Πραγματικό","m","30","30","","30","30"]
["Συμπιεστής","Type","","","","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing","","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing"]
["Διαστάσεις","Μονάδα","","Πλάτος","mm","765","765","","765","765"]
["","","","Βάθος","mm","285","285","","285","285"]
["","","","Ύψος","mm","550","550","","550","550"]
["Βάρος","Μονάδα","","","kg","38","38","","42","42"]
["Power supply","Φάση","","","","1~","1~","","1~","1~"]
["","Συχνότητα","","","Hz","50","50","","50","50"]
["","Τάση","","","V","220-240","220-240","","220-240","220-240"]
["Σημειώσεις","","","","","(1) - Περιέχει φθοριούχα αέρια του θερμοκηπίου","(1) - Περιέχει φθοριούχα αέρια του θερμοκηπίου","","(1) - Περιέχει φθοριούχα αέρια του θερμοκηπίου","(1) - Περιέχει φθοριούχα αέρια του θερμοκηπίου"]
["Διαστάσεις","Μονάδα","","Διαστάσεις-=-Μονάδα-=-Ύψος-=-χιλ.","mm","","","550","","","550"]
["","","","Διαστάσεις-=-Μονάδα-=-Πλάτος-=-χιλ.","mm","","","765","","","765"]
["","","","Διαστάσεις-=-Μονάδα-=-Βάθος-=-χιλ.","mm","","","285","","","285"]
["Βάρος","Μονάδα","","","kg","","","38","","","42"]
["Συμπιεστής","Type","","","","","","Ερμητικά κλειστός συμπιεστής swing","","","Ερμητικά κλειστός συμπιεστής swing"]
["Εύρος λειτουργίας","Ψύξη","Περιβάλλοντος","Ελάχ.","°CDB","","","10","","","10"]
["","","","Μέγ.","°CDB","","","46","","","46"]
["","Θέρμανση","Περιβάλλοντος","Ελάχ.","°CWB","","","-15","","","-15"]
["","","","Μέγ.","°CWB","","","15.5","","","15.5"]
["Στάθμη ηχητικής πίεσης","Ψύξη","","Ονομ.","dBA","","","47","","","48"]
["","Θέρμανση","","Ονομ.","dBA","","","48","","","50"]
["Ψυκτικό μέσο","Τύπος","","","","","","R-410A","","","R-410A"]
["","Φορτίο","","","kg","","","1.20","","","1.60"]
["","Φορτίο","","","tCO2Eq","","","2.5","","","3.3"]
["","GWP","","","","","","2087.5","","","2087.5"]
["Συνδέσεις σωληνώσεων","Μήκος σωληνώσεων","Μέγ.","OU - IU","m","","","20","","","20"]
["","Πρόσθετο φορτίο ψυκτικού","","","kg/m","","","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)","","","0,02 (για μήκος σωληνώσεων μεγαλύτερο από 20 m)"]
["","Υψομετρική διαφορά","ΕΣ.-ΕΞ.","Μέγ.","m","","","15","","","15"]
["","","ΕΣ.-ΕΣ.","Μέγ.","m","","","7.5","","","7.5"]
["","Συνολικό μήκος σωληνώσεων","Σύστημα","Πραγματικό","m","","","30","","","30"]
["Στάνταρτ εξαρτήματα","Installation manual","","","","","","1","","","1"]
["","Drain plug","","","","","","1","","","1"]
["","Screw bag","","","","","","1","","","1"]
["Τροφοδοσία ισχύος","Φάση","","","","","","1~","","","1~"]
["","Συχνότητα","","","Hz","","","50","","","50"]
["","Τάση","","","V","","","220-240","","","220-240"]
["Στάνταρτ εξαρτήματα","Συγκρότημα συστολής","","","","","","","1","1"]
["","Reducer assembly","","","","","","","","","1"]