{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":8,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EBLA09-14D3V3"]
[]
[]
[]
[]
["","","","","","EBLA09DA3V3","EBLA11DA3V3","EBLA14DA3V3"]
["Απόδοση θέρμανσης","Ονομ.","","","kW","9.37 (1), 9.00 (2)","10.6 (1), 9.82 (2)","12.0 (1), 12.5 (2)"]
["Απόδοση ψύξης","Ονομ.","","","kW","9.35 (3), 9.10 (4)","11.6 (3), 11.5 (4)","12.8 (3), 12.7 (4)"]
["Απόδοση θερμαντήρα","Βήμα 1","","","kW","3","3","3"]
["Ισχύς εισόδου","Ψύξη","","Ονομ.","kW","2.79 (3), 1.71 (4)","3.56 (3), 2.17 (4)","4.06 (3), 2.51 (4)"]
["","Θέρμανση","","Ονομ.","kW","1.91 (1), 2.43 (2)","2.18 (1), 2.68 (2)","2.46 (1), 3.42 (2)"]
["COP","","","","","4.91 (1), 3.71 (2)","4.83 (1), 3.66 (2)","4.87 (1), 3.64 (2)"]
["EER","","","","","3.35 (3), 5.34 (4)","3.26 (3), 5.31 (4)","3.16 (3), 5.04 (4)"]
["Διαστάσεις","Μονάδα","","Ύψος","mm","870","870","870"]
["","","","Πλάτος","mm","1380","1380","1380"]
["","","","Βάθος","mm","460","460","460"]
["Βάρος","Μονάδα","","","kg","149","149","149"]
["Ανεμιστήρας","Ταχύτητα ροής αέρα","Θέρμανση","Υψ.","m³/min","48.0","55.8","70.4"]
["","","Ψύξη","Υψ.","m³/min","63.1","70.4","85.0"]
["Εύρος λειτουργίας","Θέρμανση","Πλευρά νερού","Ελάχ.","°C","15 (6)","15 (6)","15 (6)"]
["","","","Μέγ.","°C","60 (6)","60 (6)","60 (6)"]
["","Ψύξη","Περιβάλλοντος","Ελάχ.","°CDB","10","10","10"]
["","","","Μέγ.","°CDB","43","43","43"]
["","","Πλευρά νερού","Ελάχ.","°C","5","5","5"]
["","","","Μέγ.","°C","22","22","22"]
["","Ζεστό νερό χρήσης","Περιβάλλοντος","Ελάχ.","°CDB","-25","-25","-25"]
["","","","Μέγ.","°CDB","35","35","35"]
["","","Πλευρά νερού","Ελάχ.","°C","25","25","25"]
["","","","Μέγ.","°C","55 (6)","55 (6)","55 (6)"]
["Ψυκτικό μέσο","Τύπος","","","","R-32","R-32","R-32"]
["","GWP","","","","675","675","675"]
["","Φορτίο","","","kg","3.80","3.80","3.80"]
["","Φορτίο","","","tCO2Eq","2.57","2.57","2.57"]
["Θέρμανση χώρου","Εξαγωγή νερού μέσου κλίματος 55°C","Γενικά","SCOP","","3.44","3.37","3.42"]
["","","","Κατηγορία εποχιακής απόδοσης θέρμανσης χώρου","","A++","A++","A++"]
["","Εξαγωγή νερού μέσου κλίματος 35°C","Γενικά","SCOP","","4.82","4.73","4.70"]
["","","","Κατηγορία εποχιακής απόδοσης θέρμανσης χώρου","","A+++","A+++","A+++"]
["Εύρος ενεργειακής αποδοτικότητας","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Εξάρτημα συμπιεστή","Γενική τροφοδοσία ρεύματος","","Φάση","","1~","1~","1~"]
["","","","Τάση","V","230","230","230"]
["Τροφοδοσία ισχύος","Όνομα","","","","V3","V3","V3"]
["","Φάση","","","","1~","1~","1~"]
["","Συχνότητα","","","Hz","50","50","50"]
["","Τάση","","","V","230","230","230"]
["Σημειώσεις","","","","","(1) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(2) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Συνθήκη: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(3) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(3) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB","(3) - Ψύξη: EW 12°C; LW 7°C; συνθήκες περιβάλλοντος: 35°CDB"]
["","","","","","(4) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(4) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB","(4) - Ψύξη: EW 23°C; LW 18°C; συνθήκες περιβάλλοντος: 35°CDB"]
["","","","","","(5) - Κατά EN14825","(5) - Κατά EN14825","(5) - Κατά EN14825"]
["","","","","","(6) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(6) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας","(6) - Για περισσότερες λεπτομέρειες, δείτε το σχέδιο εύρους λειτουργίας"]
["","","","","","(7) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(7) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης.","(7) - Εξαρτάται από την κατάσταση λειτουργίας,  συμβουλευθείτε το εγχειρίδιο εγκατάστασης."]