{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":57,"n_cols":12,"rows_kept":57,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FBA-A(9)"]
[]
[]
[]
[]
["","","","","","FBA35A2VEB9","FBA50A2VEB9","FBA60A2VEB9","FBA71A2VEB9","FBA100A2VEB","FBA125A2VEB","FBA140A2VEB"]
["Απόδοση ψύξης","Συνολική απόδοση","","Ονομ.","kW","","","","","","14.00","15.40"]
["Απόδοση σε λειτουργία θέρμανσης","Συνολική απόδοση","","Ονομ.","kW","","","","","","13.5","15.5"]
["Περίβλημα","Χρώμα","","","","Άβαφο (γαλβανισμένο)","Άβαφο (γαλβανισμένο)","Άβαφο (γαλβανισμένο)","Άβαφο (γαλβανισμένο)","Άβαφο (γαλβανισμένο)","Άβαφο (γαλβανισμένο)","Άβαφο (γαλβανισμένο)"]
["","Υλικό","","","","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα","Γαλβανισμένο χαλυβδοέλασμα"]
["Διαστάσεις","Μονάδα","","Ύψος","mm","245","245","245","245","245","245","245"]
["","","","Πλάτος","mm","700","700","1000","1000","1400","1400","1400"]
["","","","Βάθος","mm","800","800","800","800","800","800","800"]
["Βάρος","Μονάδα","","","kg","28.0","28.0","35.0","35.0","46.0","46.0","46.0"]
["Ανεμιστήρας","Ταχύτητα ροής αέρα","Ψύξη","Υψ.","m³/min","15.0","15.0","18.0","18.0","29.0","34.0","34.0"]
["","","","Μέτρια","m³/min","12.5","12.5","15.0","15.0","24.5","29.0","29.0"]
["","","","Χαμηλή","m³/min","10.5","10.5","12.5","12.5","20.0","23.5","23.5"]
["","","Θέρμανση","Υψ.","m³/min","15.0","15.0","18.0","18.0","29.0","34.0","34.0"]
["","","","Μέτρια","m³/min","12.5","12.5","15.0","15.0","24.5","29.0","29.0"]
["","","","Χαμηλή","m³/min","10.5","10.5","12.5","12.5","20.0","23.5","23.5"]
["","Εξωτερική στατική πίεση","","Ονομ.","Pa","30","30","30","30","40","50","50"]
["Στάθμη ηχητικής ισχύος","Ψύξη","","","dBA","60.0","60.0","56.0","56.0","58.0","62.0","62.0"]
["Στάθμη ηχητικής πίεσης","Ψύξη","","Υψ.","dBA","35.0","35.0","30.0","30.0","34.0","37.0","37.0"]
["","","","Μέτρια","dBA","32.0","32.0","28.0","28.0","32.0","35.0","35.0"]
["","","","Χαμηλή","dBA","29.0","29.0","25.0","25.0","30.0","32.0","32.0"]
["","Θέρμανση","","Υψ.","dBA","37.0","37.0","31.0","31.0","36.0","38.0","38.0"]
["","","","Μέτρια","dBA","34.0","34.0","28.0","28.0","33.0","35.0","35.0"]
["","","","Χαμηλή","dBA","29.0","29.0","25.0","25.0","30.0","32.0","32.0"]
["Συνδέσεις σωληνώσεων","Υγρό","","ΕΞ.ΔΙΑΜ.","mm","6.35","6.35","6.35","9.52","9.52","9.52","9.52"]
["","Αέριο","","ΕΞ.ΔΙΑΜ.","mm","9.52","12.70","12.70","15.90","15.90","15.90","15.90"]
["","Αποχέτευση","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["Ύψος αντλίας συμπυκνωμάτων","mm","","","","625","625","625","625","625","625","625"]
["Χειριστήρια","Τηλεχειριστήριο υπερύθρων","","","","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66"]
["","Τηλεχειριστήριο με καλώδιο","","","","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52"]
["Στάνταρτ εξαρτήματα","Installation manual","","","","1","1","1","","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","","8","8","8"]
["","Operation manual","","","","1","1","1","","1","1","1"]
["","Clamps","","","","4","4","4","","4","4","4"]
["","Drain hose","","","","1","1","1","","1","1","1"]
["","Insulation for fitting","","","","2","2","2","","2","2","2"]
["","Metal clamp for drain hose","","","","1","1","1","","1","1","1"]
["","Screws","","","","40","40","40","","40","40","40"]
["","Sealing pads","","","","5","5","5","","5","5","5"]
["Τροφοδοσία ισχύος","Φάση","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Συχνότητα","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Τάση","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Στάνταρτ εξαρτήματα","Εγχειρίδιο εγκατάστασης","","","","","","","1"]
["","Ροδέλα για στήριγμα ανάρτησης","","","","","","","8"]
["","Εγχειρίδιο χειρισμού","","","","","","","1"]
["","Σφιγκτήρες","","","","","","","4"]
["","Εύκαμπτος σωλήνας αποστράγγισης συμπυκνωμάτων","","","","","","","1"]
["","Μόνωση συνδέσμου","","","","","","","2"]
["","Μεταλλικός σφιγκτήρας εύκαμπτου σωλήνα αποστράγγισης συμπυκνωμάτων","","","","","","","1"]
["","Κοχλίες","","","","","","","40"]
["","Φύλλα στεγανοποίησης","","","","","","","5"]
["Σημειώσεις","","","","","","","","(1) - Η στάθμη ηχητικής ισχύος είναι μία απόλυτη τιμή που αντιστοιχεί στην ισχύ που παράγεται από μία ηχητική πηγή.","","(1) - Η στάθμη ηχητικής ισχύος είναι μία απόλυτη τιμή που αντιστοιχεί στην ισχύ που παράγεται από μία ηχητική πηγή."]
["","","","","","","","","(2) - Συμβουλευτείτε τα ξεχωριστά σχέδια για τα ηλεκτρολογικά χαρακτηριστικά","","(2) - Συμβουλευτείτε τα ξεχωριστά σχέδια για τα ηλεκτρολογικά χαρακτηριστικά"]