{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":11,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXV-ATV3"]
[]
[]
[]
[]
["","","","","","FWXV10AATV3","FWXV10ABTV3","FWXV15AATV3","FWXV15ABTV3","FWXV20AATV3","FWXV20ABTV3"]
["Απόδοση σε λειτουργία ψύξης","7/12°C","","Ελάχ.","kW","0.66","0.78","1.30","1.10","1.82","1.13"]
["Απόδοση ψύξης","7/12°C","","Μεσ.","kW","1.36","1.11","2.16","1.65","2.52","1.98"]
["","","","Μέγ.","kW","1.77","1.62","2.89","2.64","3.20","2.99"]
["Απόδοση αισθητής θερμότητας","7/12°C","","Ελάχ.","kW","0.39","0.58","0.99","0.82","1.22","0.85"]
["","","","Μεσ.","kW","0.98","0.71","1.53","1.15","1.55","1.55"]
["","","","Μέγ.","kW","1.33","1.25","2.10","1.91","1.78","2.33"]
["Απόδοση σε λειτουργία θέρμανσης","45/40°C","","Ελάχ.","kW","0.95","0.87","1.24","1.12","1.90","1.11"]
["","","","Μεσ.","kW","1.63","1.27","2.33","1.83","3.05","2.32"]
["","","","Μέγ.","kW","2.18","1.96","3.11","2.86","3.88","3.50"]
["Απορροφ. ισχύς","Ελάχ.","","","kW","0","0.01","0","0.01","0.01","0.01"]
["","Μεσ.","","","kW","","0.01","","0.01","","0.01"]
["","Μέγ.","","","kW","0.02","0.02","0.02","0.03","0.03","0.03"]
["Ταχύτητα ανεμιστήρα","Ελάχ.","","","rpm","118.00","720.00","180.00","720.00","246.00","720.00"]
["","Μεσ.","","","rpm","210.00","1220.00","318.00","1220.00","410.00","1220.00"]
["","Μέγ.","","","rpm","294.00","1700.00","438.00","1700.00","566.00","1700.00"]
["Περίβλημα","Χρώμα","","","","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003"]
["","Υλικό","","","","Λαμαρίνα","Λαμαρίνα","Λαμαρίνα","Λαμαρίνα","Λαμαρίνα","Λαμαρίνα"]
["Διαστάσεις","Μονάδα","","Διαστάσεις-=-Μονάδα-=-Ύψος-=-χιλ.","mm","601","601","601","601","601","601"]
["","","","Διαστάσεις-=-Μονάδα-=-Πλάτος-=-χιλ.","mm","999","999","1200","1199","1400","1399"]
["","","","Διαστάσεις-=-Μονάδα-=-Βάθος-=-χιλ.","mm","135","135","135","135","135","135"]
["","Μονάδα με στεγανοποίηση","","Διαστάσεις-=-Μονάδα με στεγανοποίηση-=-Ύψος-=-χιλ.","mm","690","690","690","690","690","690"]
["","","","Διαστάσεις-=-Μονάδα με στεγανοποίηση-=-Πλάτος-=-χιλ.","mm","1230","1230","1430","1430","1630","1630"]
["","","","Διαστάσεις-=-Μονάδα με στεγανοποίηση-=-Βάθος-=-χιλ.","mm","210","210","210","210","210","210"]
["Βάρος","Μονάδα","","","kg","20","20","23","23","26","26"]
["","Μονάδα με στεγανοποίηση","","","kg","21","21","24","24","27","27"]
["Συσκευασία","Υλικό","","","","Κιβώτιο","Κιβώτιο","Κιβώτιο","Κιβώτιο","Κιβώτιο","Κιβώτιο"]
["","Βάρος","","","kg","1","1","1","1","1","1"]
["Εναλλάκτης θερμότητας","Ποσότητα","","","","1","1","1","1","1","1"]
["","Όγκος εσωτερικής σερπαντίνας","","","l","0.8","0.8","1.1","1.1","1.5","1.5"]
["","Φόρτιση","","Πίεση λειτουργίας","bar","10","10","10","10","10","10"]
["Κύκλωμα νερού","Διάμετρος συνδέσεων σωληνώσεων","","","in","3/4","3/4","3/4","3/4","3/4","3/4"]
["","Υλικό σωληνώσεων","","","","Ορείχαλκος (CW617N)","COPPER","Ορείχαλκος (CW617N)","COPPER","Ορείχαλκος (CW617N)","COPPER"]
["","Πίεση","Θέρμανση","Μέγ.","bar","10","10","10","10","10","10"]
["Κύκλωμα νερού - πτώση πίεσης νερού","Θέρμανση","45/40°C","Ελάχ.","kPa","1.30","7.00","8.60","9.00","3.80","8.00"]
["","","","Μεσ.","kPa","4.20","8.00","3.30","14.00","11.20","15.00"]
["","","","Μέγ.","kPa","7.20","11.00","11.50","23.00","21.30","22.00"]
["","Ψύξη","7/12°C","Ελάχ.","kPa","1.20","7.00","4.30","9.00","2.10","8.00"]
["","","","Μεσ.","kPa","2.80","8.00","19.30","14.00","13.10","15.00"]
["","","","Μέγ.","kPa","2.90","11.00","27.00","23.00","24.00","22.00"]
["Κύκλωμα νερού - ταχύτητα ροής νερού","Θέρμανση","45/40°C","Ελάχ.","kg/h","163.50","150.00","212.50","200.00","327.00","190.00"]
["","","","Μεσ.","kg/h","280.30","220.00","401.10","320.00","524.60","400.00"]
["","","","Μέγ.","kg/h","374.10","340.00","534.50","500.00","667.50","610.00"]
["","Ψύξη","7/12°C","Ελάχ.","kg/h","113.50","130.00","223.70","190.00","313.00","190.00"]
["","","","Μεσ.","kg/h","234.10","190.00","371.70","280.00","433.60","340.00"]
["","","","Μέγ.","kg/h","303.60","280.00","496.60","450.00","550.60","510.00"]
["Στάθμη ηχητικής ισχύος","Ελάχ.","","","dBA","34","40","35","42","35","43"]
["","Μεσ.","","","dBA","43","47","43","49","44","50"]
["Sound power level","Μέγ.","","","dBA","51.0","56.0","53.0","57.0","55.0","58.0"]
["Εύρος λειτουργίας","Θέρμανση","Πλευρά νερού","Ελάχ.","°C","30","30","30","30","30","30"]
["","","","Μέγ.","°C","85","85","85","85","85","85"]
["","Ψύξη","Πλευρά νερού","Ελάχ.","°C","5","5","5","5","5","5"]
["","","","Μέγ.","°C","18","18","18","18","18","18"]
["","Εσωτερική εγκατάσταση","Περιβάλλον","Ελάχ.","°CDB","0","0","0","0","0","0"]
["","","","Μέγ.","°CDB","45","45","45","45","45","45"]
["Συστήματα ελέγχου","Infrared remote control","","","","Όχι","Όχι","Όχι","Όχι","Όχι","Όχι"]
["Χειριστήρια","Ενσωματωμένη στην εσωτερική μονάδα","","","","Ναι","Ναι","Ναι","Ναι","Ναι","Ναι"]
["Τροφοδοσία ισχύος","Φάση","","","","1~","1~","1~","1~","1~","1~"]
["","Συχνότητα","","","Hz","50","50","50","50","50","50"]
["","Τάση","","","V","230","230","230","230","230","230"]
["Κατανάλωση ηλεκτρικού ρεύματος","Μέγ.","","","W","19","19","20","25","29","31"]
["","Αναμονή","","","W","3","3","4","4","5","5"]
["Ρεύμα","Μέγιστο ρεύμα λειτουργίας","","Θέρμανση","A","0.2","0.15","0.2","0.21","0.3","0.27"]
["","Μέγ. ρεύμα λειτ.","","Ψύξη","A","0.2","0.15","0.2","0.21","0.3","0.27"]