{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":13,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NV1"]
[]
[]
[]
[]
["","","","","","RZAG71N7V1B","RZAG71N2V1B","RZAG100N7V1B","RZAG100N2V1B","RZAG125N7V1B","RZAG125N2V1B","RZAG140N7V1B","RZAG140N2V1B"]
["Διαστάσεις","Μονάδα","","Διαστάσεις-=-Μονάδα-=-Ύψος-=-χιλ.","χιλ.","870","870","870","870","870","870","870","870"]
["","","","Διαστάσεις-=-Μονάδα-=-Πλάτος-=-χιλ.","χιλ.","1100","1100","1100","1100","1100","1100","1100","1100"]
["","","","Διαστάσεις-=-Μονάδα-=-Βάθος-=-χιλ.","χιλ.","460","460","460","460","460","460","460","460"]
["Βάρος","Μονάδα","","","kg","81","81","85","85","95","95","95","95"]
["Συμπιεστής","Type","","","","","","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing"]
["Εύρος λειτουργίας","Ψύξη","Περιβάλλοντος","Ελάχ.","°CDB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Μέγ.","°CDB","52","52","52","52","52","52","52","52"]
["","Θέρμανση","Περιβάλλοντος","Ελάχ.","°CWB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Μέγ.","°CWB","18","18","18","18","18","18","18","18"]
["Στάθμη ηχητικής ισχύος","Ψύξη","","","dBA","64","64","66","66","69","69","70","70"]
["","Θέρμανση","","","dBA","","","","","68 (1)","68 (1)","71 (1)","71 (1)"]
["Στάθμη ηχητικής πίεσης","Ψύξη","","Ονομ.","dBA","46","46","47","47","49","49","50","50"]
["","Θέρμανση","","Ονομ.","dBA","48","48","50","50","52","52","52","52"]
["Ψυκτικό μέσο","Τύπος","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Φορτίο","","","kg","3.2","3.20","3.2","3.20","3.7","3.70","3.7","3.70"]
["","GWP","","","","675","675","675","675","675","675","675","675"]
["","Φορτίο","","","tCO2Eq","2.16","2.16","2.16","2.16","2.5","2.50","2.5","2.50"]
["Συνδέσεις σωληνώσεων","Υγρό","","Συνδέσεις σωληνώσεων-=-Υγρό-=-ΕΞ.ΔΙΑΜ.-=-χιλ.","χιλ.","10","10","10","10","10","10","10","10"]
["","Αέριο","","Συνδέσεις σωληνώσεων-=-Αέριο-=-ΕΞ.ΔΙΑΜ.-=-χιλ.","χιλ.","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["","Μήκος σωληνώσεων","Μέγ.","OU - IU","m","55","55","85","85","85","85","85","85"]
["","","Σύστημα","Ισοδύναμο","m","75","75","100","100","100","100","100","100"]
["","","","Χωρίς φορτίο","m","40","40","40","40","40","40","40","40"]
["","Πρόσθετο φορτίο ψυκτικού","","","kg/m","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης","Βλ. εγχειρίδιο εγκατάστασης"]
["","Υψομετρική διαφορά","ΕΣ.-ΕΞ.","Μέγ.","m","30","30","30","30","30","30","30","30"]
["","","ΕΣ.-ΕΣ.","Μέγ.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Στάνταρτ εξαρτήματα","Installation manual","","","","1","1","1","1","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1","1","1","1"]
["","Peel off F-gas label","","","","1","1","1","1","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2","2","2","2","2"]
["Τροφοδοσία ισχύος","Φάση","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Συχνότητα","","","Hz","50","50","50","50","50","50","50","50"]
["","Τάση","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Ρεύμα - 50Hz","Μέγιστα αμπέρ ασφάλειας (MFA)","","","A","20","20","32","32","32","32","32","32"]
["Συμπιεστής","Τύπος","","","","Ερμητικά κλειστός συμπιεστής swing","Ερμητικά κλειστός συμπιεστής swing"]
["Σημειώσεις","","","","","","","","","(1) - Σύμφωνα με ENER Lot 21","(1) - Σύμφωνα με ENER Lot 21","(1) - Σύμφωνα με ENER Lot 21","(1) - Σύμφωνα με ENER Lot 21"]