{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VH-B"]
[]
[]
[]
[]
["","","","VH1B","VH2B","VH3B","VH4/AB","VH4B","VH5B"]
["Ρεύμα εξόδου (μέγιστο)","","","19A σε 40°C (περιβάλλον)","19A σε 40°C (περιβάλλον)","19A σε 40°C (περιβάλλον)","19A σε 40°C (περιβάλλον)","19A σε 40°C (περιβάλλον)","19A σε 40°C (περιβάλλον)"]
["Μονάδα που μπορεί να συνδεθεί","","","VAM150FA","VAM250FA, VAM350FB","VAM500FB, VAM650FB","VAM800FB, VAM1000FB","VAM800FB, VAM1000FB","VAM1500FB, VAM2000FB"]
["Ένδειξη LED","","","Ισχύς ΟΝ - Κίτρινο, Θερμαντήρας ON - Κόκκινο (σταθερό ή αναβοσβήνει, δείχνει έλεγχο παλμών), Σφάλμα ροής αέρα - Κόκκινο","Ισχύς ΟΝ - Κίτρινο, Θερμαντήρας ON - Κόκκινο (σταθερό ή αναβοσβήνει, δείχνει έλεγχο παλμών), Σφάλμα ροής αέρα - Κόκκινο","Ισχύς ΟΝ - Κίτρινο, Θερμαντήρας ON - Κόκκινο (σταθερό ή αναβοσβήνει, δείχνει έλεγχο παλμών), Σφάλμα ροής αέρα - Κόκκινο","Ισχύς ΟΝ - Κίτρινο, Θερμαντήρας ON - Κόκκινο (σταθερό ή αναβοσβήνει, δείχνει έλεγχο παλμών), Σφάλμα ροής αέρα - Κόκκινο","Ισχύς ΟΝ - Κίτρινο, Θερμαντήρας ON - Κόκκινο (σταθερό ή αναβοσβήνει, δείχνει έλεγχο παλμών), Σφάλμα ροής αέρα - Κόκκινο","Ισχύς ΟΝ - Κίτρινο, Θερμαντήρας ON - Κόκκινο (σταθερό ή αναβοσβήνει, δείχνει έλεγχο παλμών), Σφάλμα ροής αέρα - Κόκκινο"]
["Ρελέ λειτουργίας","","","1A 120V AC ή 1A 24V DC","1A 120V AC ή 1A 24V DC","1A 120V AC ή 1A 24V DC","1A 120V AC ή 1A 24V DC","1A 120V AC ή 1A 24V DC","1A 120V AC ή 1A 24V DC"]
["Διάμετρος αγωγού","mm","","100","150","200","250","250","350"]
["Απόδοση","kW","","1.0","1.0","1.0","2.5","1.5","2.5"]
["Οπές συναρμολόγησης","","","98mm x 181mm κέντρο, οπές 5mm Ø","98mm x 181mm κέντρο, οπές 5mm Ø","98mm x 181mm κέντρο, οπές 5mm Ø","98mm x 181mm κέντρο, οπές 5mm Ø","98mm x 181mm κέντρο, οπές 5mm Ø","98mm x 181mm κέντρα 5mm _ οπές"]
["Μέγιστη θερμοκρασία περιβάλλοντος δίπλα στο κιβώτιο ακροδεκτών","","","35°C (κατά τη διάρκεια της λειτουργίας)","35°C (κατά τη διάρκεια της λειτουργίας)","35°C (κατά τη διάρκεια της λειτουργίας)","35°C (κατά τη διάρκεια της λειτουργίας)","35°C (κατά τη διάρκεια της λειτουργίας)","35°C (κατά τη διάρκεια της λειτουργίας)"]
["Αισθητήρας θερμοκρασίας","","","5k ohm σε 25°C (πίνακας 502 1T)","5k ohm σε 25°C (πίνακας 502 1T)","5k ohm σε 25°C (πίνακας 502 1T)","5k ohm σε 25°C (πίνακας 502 1T)","5k ohm σε 25°C (πίνακας 502 1T)","5k ohm σε 25°C (πίνακας 502 1T)"]
["Είσοδος σημείου ρύθμισης BMS","","","0-10VDC","0-10VDC","0-10VDC","0-10VDC","0-10VDC","0-10VDC"]
["Εύρος ελέγχου θερμοκρασίας","","","0 έως 40°C / (0-10V 0-100%)","0 έως 40°C / (0-10V 0-100%)","0 έως 40°C / (0-10V 0-100%)","0 έως 40°C / (0-10V 0-100%)","0 έως 40°C / (0-10V 0-100%)","0 έως 40°C / (0-10V 0-100%)"]
["Ασφάλεια ελέγχου","","","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA"]
["Power supply","Συχνότητα","Hz","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Τάση","V","220/250","220/250","220/250","220/250","220/250","220/250"]